## COM CALCULATOR
MAU and PCU Center of Mass Calculator | [9 empty] | REV. #6: 05/30/2018 |  |  |  | Unit Information:
Equipment Type: | MAU | [12 empty] | MAU Module | Multiplier | Equipment Type
Position from Left: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  |  | None | 1 | MAU
Type of Module: | None | None | None | None | None | None | None | None | None | None |  |  |  | MAU Blower | 0.66667 | PCU
Size: | [13 empty] | Direct Fired Module | 0.5
Motor HP (blower module only): | [13 empty] | Electric Heater Module | 0.5
Condenser on top of module: | [13 empty] | IBT Module | 0.5
Individual Weight: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summation of Loads: |  | DX Coil Module | 0.5
Individual Width: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Hot Water Coil Module | 0.5
Individual Moment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Chilled Water Coil Module | 0.5
[14 empty] | Steam Coil | 0.5
Total Weight: |  | 0 | LBS. | [10 empty] | Standard Evaporative Intake | 0.5
Center Of Mass: |  | #DIV/0! | INCHES (Distance from left side of Unit) | [10 empty] | Celdek Evaporative Intake | 0.5
Intake End Corner Weights |  | #DIV/0! | LBS. (Standard Right > Left Config Assumed) | [10 empty] | V-Bank Filter Intake | 0.5
Discharge End Corner Weights |  | #DIV/0! | LBS. (Standard Right > Left Config Assumed) | [10 empty] | Screened Intake | 0.33333
[14 empty] | Intake Hood | 0.33333
[14 empty] | Downturn Plenum | 0.5
[14 empty] | Trunkline | 0.5
[14 empty] | Mixing box/Condenser support | 0.5
[14 empty] | PCU Module | Multiplier
[14 empty] | None | 1
[14 empty] | PCU Blower | 0.66667
[14 empty] | Pre-Filter Module | 0.5
[14 empty] | High Efficiency Module | 0.5
[14 empty] | HEPA Filter Module | 0.5
[14 empty] | Odor Control Filter Module | 0.5
[14 empty] | Odor Control Filter LAST Module | 0.5
[14 empty] | Odor Control Panel Filter Module | 0.5
[14 empty] | Discharge Cover | 0.33333
Makeup Air Individual Module Reference Information:
BLOWER MODULES:
Unit Spec | Blower Size
| 10" | 12" | 15" | 15"D | 18" | 20" | 20"D | 24"D | 25" | 30"D | 36"D |  | MAU Blower | Weight (LBS.) | Width (IN.)
Weight (LBS.) | 205 | 350 | 360 | 260 | 435 | 735 | 428 | 531 | 1105 | 1067 | 1271 |  | 10" | 205 | 32.125
Width (IN.) | 32.125 | 40.125 | 40.125 | 32.125 | 45.125 | 64.1875 | 40.125 | 42.125 | 74.1875 | 64.1875 | 74.1875 |  | 12" | 350 | 40.125
[13 empty] | 15" | 360 | 40.125
DIRECT FIRED HEATING MODULES: | [12 empty] | 15"D | 260 | 32.125
Unit Spec | Model | [11 empty] | 18" | 435 | 45.125
| D1.250 | D1.500 | D2.500 | D2.750 | D3.750 | D3.1000 | D4.1000 | D4.1500 | D5.2000 | D5.2500 |  |  | 20" | 735 | 64.1875
Weight (LBS.) | 345 | 350 | 420 | 425 | 450 | 455 | 690 | 705 | 830 | 845 |  |  | 20"D | 428 | 40.125
Width (IN.) | 42.125 | 42.125 | 42.125 | 42.125 | 42.125 | 42.125 | 54.1875 | 54.1875 | 54.1875 | 54.1875 |  |  | 24"D | 531 | 45.125
[13 empty] | 25" | 1105 | 74.1875
[13 empty] | 30"D | 1067 | 64.1875
ELECTRIC HEATER MODULES: | [12 empty] | 36"D | 1271 | 74.1875
Unit Spec | Model
| E1.10 | E1.20 | E1.204 | E1.36 | E2.36 | E2.69 | E3.83 | E4.155 | E5.235
Weight (LBS.) | 300 | 300 | 300 | 300 | 380 | 380 | 450 | 710 | 840 |  |  |  | Direct Fired Module
Width (IN.) | 42.125 | 42.125 | 42.125 | 42.125 | 42.125 | 42.125 | 42.125 | 54.1875 | 54.1875 |  |  |  | D1.250 | 345 | 42.125
[13 empty] | D1.500 | 350 | 42.125
[13 empty] | D2.500 | 420 | 42.125
INDIRECT FIRED HEATING MODULES: | [12 empty] | D2.750 | 425 | 42.125
Unit Spec | Model IBT | [11 empty] | D3.500 | 445 | 42.125
| 1-.150 | 1-.200 | 1-.300-150-150 | 1-.400-200-200 | 2-.200 | 2-.300 | 2-.400 | 2-.400-200-200 | 2-.600-300-300 |  |  |  | D3.750 | 450 | 42.125
Weight (LBS.) | 567 | 597 | 652 | 726 | 595 | 687 | 766 | 654 | 808 |  |  |  | D3.1000 | 455 | 42.125
Width (IN.) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  |  |  | D4.1000 | 690 | 54.1875
[13 empty] | D4.1500 | 705 | 54.1875
| 2-.800-400-400 | 3-.400 | 3.-600-300-300 | 3.-800-400-400 | 3.-1000-300-300-400 | 3.-1200-400-400-400 | 4.-800-400-400 | 4.1000-300-300-400 | 4.-1200-400-400-400 |  |  |  | D5.2000 | 830 | 54.1875
Weight (LBS.) | 921 | 947 | 1065 | 1203 | 1942 | 2054 | 1154 | 2037 | 2149 |  |  |  | D5.2500 | 845 | 54.1875
Width (IN.) | 60 | 60 | 60 | 60 | 120 | 120 | 60 | 120 | 120
| 4.-1400-300-300-400-400 | 4.-1600-400-400-400-400 | 5-.800-400-400 | 5.-1000-300-300-400 | 5.-1200-400-400-400 | 5.-1400-300-300-400-400 | 5.-1600-400-400-400-400
Weight (LBS.) | 2261 | 2373 | 1257 | 2029 | 2141 | 2253 | 2365 | [5 empty] | Electric Heater Module
Width (IN.) | 120 | 120 | 60 | 120 | 120 | 120 | 120 | [5 empty] | E1.10 | 300 | 42.125
[13 empty] | E1.20 | 300 | 42.125
[13 empty] | E1.204 | 300 | 42.125
DX COIL MODULES: | [12 empty] | E1.36 | 300 | 42.125
Unit Spec | Model | [11 empty] | E2.36 | 380 | 42.125
| DXM1 | DXM2 | DXM3 | DXM4 | DXM5 | [7 empty] | E2.69 | 380 | 42.125
Weight (LBS.) | 355 | 430 | 505 | 780 | 905 | [7 empty] | E3.83 | 450 | 42.125
Width (IN.) | 42.125 | 42.125 | 42.125 | 54.1875 | 54.1875 | [7 empty] | E4.155 | 710 | 54.1875
[13 empty] | E5.235 | 840 | 54.1875
HOT WATER COIL MODULES:
Unit Spec | Model | [11 empty] | IBT Module
| HWCM1 | HWCM2 | HWCM3 | HWCM4 | HWCM5 | [7 empty] | 1-.150 | 567 | 60
Weight (LBS.) | 160 | 220 | 260 | 435 | 525 | [7 empty] | 1-.200 | 597 | 60
Width (IN.) | 42.125 | 42.125 | 42.125 | 54.1875 | 54.1875 | [7 empty] | 1-.300-150-150 | 652 | 60
[13 empty] | 1-.400-200-200 | 726 | 60
[13 empty] | 2-.200 | 595 | 60
CHILLED WATER COIL MODULES: | [12 empty] | 2-.300 | 687 | 60
Unit Spec | Model | [11 empty] | 2-.400 | 766 | 60
| CWCM1 | CWCM2 | CWCM3 | CWCM4 | CWCM5 | [7 empty] | 2-.400-200-200 | 654 | 60
Weight (LBS.) | 355 | 435 | 575 | 790 | 905 | [7 empty] | 2-.600-300-300 | 808 | 60
Width (IN.) | 42.125 | 42.125 | 42.125 | 54.1875 | 54.1875 | [7 empty] | 2-.800-400-400 | 921 | 60
[13 empty] | 3-.400 | 947 | 60
[13 empty] | 3.-600-300-300 | 1065 | 60
STEAM COIL MODULES: | [12 empty] | 3.-800-400-400 | 1203 | 60
Unit Spec | Model | [11 empty] | 3.-1000-300-300-400 | 1942 | 120
| SCM1 | SCM2 | SCM3 | SCM4 | SCM5 | [7 empty] | 3.-1200-400-400-400 | 2054 | 120
Weight (LBS.) | 160 | 220 | 255 | 410 | 520 | [7 empty] | 4.-400 | 937 | 60
Width (IN.) | 42.125 | 42.125 | 42.125 | 54.1875 | 54.1875 | [7 empty] | 4.-800-400-400 | 1154 | 60
[13 empty] | 4.1000-300-300-400 | 2037 | 120
[13 empty] | 4.-1200-400-400-400 | 2149 | 120
STANDARD EVAPORATIVE COOLER INTAKE: | [12 empty] | 4.-1400-300-300-400-400 | 2261 | 120
Unit Spec | Model | [11 empty] | 4.-1600-400-400-400-400 | 2373 | 120
| ECI-01 | ECI-02 | ECI-03 | ECI-04 | ECI-05 | [7 empty] | 5.-400 | 1040 | 60
Weight (LBS.) | 130 | 180 | 240 | 330 | 405 | [7 empty] | 5-.800-400-400 | 1257 | 60
Width (IN.) | 32.125 | 32.125 | 38.125 | 35.25 | 35.25 | [7 empty] | 5.-1000-300-300-400 | 2029 | 120
[13 empty] | 5.-1200-400-400-400 | 2141 | 120
[13 empty] | 5.-1400-300-300-400-400 | 2253 | 120
CELDEK EVAPORATIVE COOLER INTAKE: | [12 empty] | 5.-1600-400-400-400-400 | 2365 | 120
Unit Spec | Model
| CDI-01 | CDI-02 | CDI-03 | CDI-04 | CDI-05
Weight (LBS.) | 135 | 175 | 230 | 300 | 365 | [7 empty] | DX Coil Module
Width (IN.) | 32.125 | 32.125 | 38.125 | 35.25 | 35.25 | [7 empty] | DXM1 | 355 | 42.125
[13 empty] | DXM2 | 430 | 42.125
[13 empty] | DXM3 | 505 | 42.125
V-BANK FILTER INTAKE: | [12 empty] | DXM4 | 780 | 54.1875
Unit Spec | Model | [11 empty] | DXM5 | 905 | 54.1875
| VBI-01 | VBI-02 | VBI-03 | VBI-04 | VBI-05
Weight (LBS.) | 95 | 135 | 165 | 235 | 295
Width (IN.) | 32.125 | 32.125 | 38.125 | 35.25 | 35.25 | [7 empty] | Hot Water Coil Module
[13 empty] | HWCM1 | 160 | 42.125
[13 empty] | HWCM2 | 220 | 42.125
SCREENED INTAKE: | [12 empty] | HWCM3 | 260 | 42.125
Unit Spec | Model | [11 empty] | HWCM4 | 435 | 54.1875
| SI-1 | SI-2 | SI-3 | SI-4 | SI-5 | [7 empty] | HWCM5 | 525 | 54.1875
Weight (LBS.) | 25 | 35 | 50 | 100 | 135
Width (IN.) | 22.375 | 30.3125 | 34.1875 | 47.25 | 49.625
Chilled Water Coil Module
[13 empty] | CWCM1 | 355 | 42.125
INTAKE HOOD: | [12 empty] | CWCM2 | 435 | 42.125
Unit Spec | Model | [11 empty] | CWCM3 | 575 | 42.125
| SFIH-01M | SFIH-02M | SFIH-03M | SFIH-04M | SFIH-05M | SFIH-01S | SFIH-02S | [5 empty] | CWCM4 | 790 | 54.1875
Weight (LBS.) | 45 | 65 | 90 | 210 | 225 | 30 | 40 | [5 empty] | CWCM5 | 905 | 54.1875
Width (IN.) | 44.375 | 53.625 | 51.625 | 76.375 | 71.375 | 25.875 | 29.25
Steam Coil
DOWNTURN PLENUM: | [12 empty] | SCM1 | 160 | 42.125
Unit Spec | Model | [11 empty] | SCM2 | 220 | 42.125
| DP-01 | DP-02 | DP-03 | DP-04 | DP-05 | [7 empty] | SCM3 | 255 | 42.125
Weight (LBS.) | 80 | 115 | 140 | 190 | 230 | [7 empty] | SCM4 | 410 | 54.1875
Width (IN.) | 18.25 | 24.25 | 24.25 | 30.25 | 30.25 | [7 empty] | SCM5 | 520 | 54.1875
TRUNKLINE: | [12 empty] | Standard Evaporative Intake
Unit Spec | Model | [11 empty] | ECI-01 | 130 | 32.125
| TL-01M | TL-02M | TL-03M | TL-04M | TL-01S | TL-02S | TL-01DF | TL-02DF | TL-03DF |  |  |  | ECI-02 | 180 | 32.125
Weight (LBS.) | 135 | 175 | 215 | 310 | 120 | 175 | 95 | 120 | 150 |  |  |  | ECI-03 | 240 | 38.125
Width (IN.) | 88 | 80 | 75 | 50 | 88 | 80 | 46 | 38 | 33 |  |  |  | ECI-04 | 330 | 35.25
[13 empty] | ECI-05 | 405 | 35.25
MIXING BOX/CONDENSER SUPPORT:
Unit Spec | Model TL-01M: Model |  |  |  | Celdek Evaporative Intake
| Model TL-01M: MB-1; Model TL-02M: MB-2; Model TL-03M: MB-3; Model TL-04M: MB-4; Model TL-01S: MB-5 |  |  |  | CDI-01 | 135 | 32.125
Weight (LBS.) | Model TL-01M: 155; Model TL-02M: 215; Model TL-03M: 280; Model TL-04M: 475; Model TL-01S: 575 |  |  |  | CDI-02 | 175 | 32.125
Width (IN.) | Model TL-01M: 42.125; Model TL-02M: 42.125; Model TL-03M: 42.125; Model TL-04M: 54.1875; Model TL-01S: 54.1875 |  |  |  | CDI-03 | 230 | 38.125
[13 empty] | CDI-04 | 300 | 35.25
[13 empty] | CDI-05 | 365 | 35.25
CONDENSERS:
Unit Spec | Model TL-01M: Model
| Model TL-01M: 2 TON; Model TL-02M: 2.5 TON; Model TL-03M: 3 TON; Model TL-04M: 5 TON |  |  |  | V-Bank Filter Intake
Weight (LBS.) | Model TL-01M: 110; Model TL-02M: 111; Model TL-03M: 141; Model TL-04M: 198; Model TL-01S: Add the condenser weight to the module that it is supported by. Use the support module |  |  |  | VBI-01 | 95 | 32.125
Width (IN.) | Model TL-01M: Base Module; Model TL-02M: Base Module; Model TL-03M: Base Module; Model TL-04M: Base Module; Model TL-01S: width for dimensional data. |  |  |  | VBI-02 | 135 | 32.125
[13 empty] | VBI-03 | 165 | 38.125
[13 empty] | VBI-04 | 235 | 35.25
Pollution Control Unit Individual Module Reference Information: | [12 empty] | VBI-05 | 295 | 35.25
POLLUTION CONTROL UNIT - BLOWER
Unit Spec | Model TL-01M: Blower Size |  |  |  | Screened Intake
| KB-10 | KB-14 | KB-18 | KB-20 | KB-25 | KB-25 | KB-32 | [5 empty] | SI-1 | 25 | 22.375
Weight (LBS.) | 215.32 | 352.13 | 451.57 | 666.44 | 1069.34 | 1069.34 | 1509 | [5 empty] | SI-2 | 35 | 30.3125
Width (IN.) | 32.125 | 40.125 | 45.125 | 64.19 | 74.19 | 74.19 | 84.19 | [5 empty] | SI-3 | 50 | 34.1875
[13 empty] | SI-4 | 100 | 47.25
POLLUTION CONTROL UNIT - PREFILTER | [12 empty] | SI-5 | 135 | 49.625
Unit Spec | Model TL-01M: Model
| PF-1 | PF-2 | PF-3 | PF-4 | PF-5 | PF-6 | PF-7
Weight (LBS.) | 160.73 | 244.12 | 300.87 | 383.2 | 427.61 | 585.09 | 811.65
Width (IN.) | 26.69 | 26.69 | 31.81 | 28 | 27.56 | 27.56 | 27.56 | [5 empty] | Intake Hood
[13 empty] | SFIH-01M | 45 | 44.375
POLLUTION CONTROL UNIT - HIGH EFFICIENCY FILTER | [12 empty] | SFIH-02M | 65 | 53.625
Unit Spec | Model TL-01M: Model |  |  |  | SFIH-03M | 90 | 51.625
| HE-1 | HE-2 | HE-3 | HE-4 | HE-5 | HE-6 | HE-7 | [5 empty] | SFIH-04M | 210 | 76.375
Weight (LBS.) | 150.23 | 223.12 | 272.87 | 348.2 | 385.61 | 522.09 | 706.65 | [5 empty] | SFIH-05M | 225 | 71.375
Width (IN.) | 26.69 | 26.69 | 31.81 | 28 | 27.56 | 27.56 | 27.56 | [5 empty] | SFIH-01S | 30 | 25.875
[13 empty] | SFIH-02S | 40 | 29.25
POLLUTION CONTROL UNIT - HEPA FILTER
Unit Spec | Model TL-01M: Model
| HEPA-1 | HEPA-2 | HEPA-3 | HEPA-4 | HEPA-5 | HEPA-6 | HEAP-7 | [5 empty] | Downturn Plenum
Weight (LBS.) | 160.73 | 244.12 | 300.87 | 383.2 | 427.61 | 585.09 | 811.65 | [5 empty] | DP-01 | 80 | 18.25
Width (IN.) | 26.69 | 26.69 | 31.81 | 28 | 27.56 | 27.56 | 27.56 | [5 empty] | DP-02 | 115 | 24.25
[13 empty] | DP-03 | 140 | 24.25
POLLUTION CONTROL UNIT - ODOR CONTROL FILTER | [12 empty] | DP-04 | 190 | 30.25
Unit Spec | Model TL-01M: Model |  |  |  | DP-05 | 230 | 30.25
| OC-1 | OC-2 | OC-3 | OC-4 | OC-5 | OC-6 | OC-7
Weight (LBS.) | 152.6 | 227.86 | 279.19 | 356.1 | 395.09 | 536.31 | 730.35
Width (IN.) | 26.69 | 26.69 | 31.81 | 28 | 27.56 | 27.56 | 27.56 | [5 empty] | Trunkline
Width if last module (IN.) | 32 | 32 | 38 | 35 | 35 | 35 | 35 | [5 empty] | TL-01M | 135 | 88
[13 empty] | TL-02M | 175 | 80
POLLUTION CONTROL UNIT - ODOR CONTROL PANEL FILTER | [12 empty] | TL-03M | 215 | 75
Unit Spec | Model TL-01M: Model |  |  |  | TL-04M | 310 | 50
| OCP-1 | OCP-2 | OCP-3 | OCP-4 | OCP-5 | OCP-6 | OCP-7 | [5 empty] | TL-01S | 120 | 88
Weight (LBS.) | 232.73 | 388.12 | 492.87 | 623.2 | 715.61 | 1017.09 | 1531.65 | [5 empty] | TL-02S | 175 | 80
Width (IN.) | 26.69 | 26.69 | 31.81 | 28 | 27.56 | 27.56 | 27.56 | [5 empty] | TL-01DF | 95 | 46
[13 empty] | TL-02DF | 120 | 38
DISCHARGE COVER - Use Triangular Intake setting | [12 empty] | TL-03DF | 150 | 33
Unit Spec | Model TL-01M: Model
| KB.DCS-1 | KB.DCS-1 | KB.DCS-3 | KB.DCS-3 | KB.DCS-3 | KB.DCS-3 | KB.DCS-4
Weight (LBS.) | 22.11 | 22.11 | 56.15 | 56.15 | 56.15 | 56.15 | 56.15 | [5 empty] | Mixing box/Condenser support
Width (IN.) | 22.375 | 22.375 | 34.1875 | 34.1875 | 34.1875 | 34.1875 | 34.1875 | [5 empty] | MB-1 | 155 | 42.125
[13 empty] | MB-2 | 215 | 42.125
POLLUTION CONTROL UNIT - MOTOR WEIGHT - add to the blower weight | [12 empty] | MB-3 | 280 | 42.125
HP | Model TL-01M: Phase; Model TL-02M: Model |  |  |  | MB-4 | 475 | 54.1875
|  | KB-10 | KB-14 | KB-18 | KB-20 | KB-25 | KB-25 | KB-32 |  |  |  |  | MB-5 | 575 | 54.1875
0.5 | 1 | 25 | 25 | - | - | - | - | -
0.75 | 1 | 25 | 25 | 25 | - | - | - | - |  |  |  |  | Condensers
1 | 1 | 33 | 33 | 33 | 33 | 33 | 33 | -
1.5 | 1 | 32 | 32 | 32 | 32 | 32 | 32 | - |  |  |  |  | 2 TON | 110 | Base Module
0.5 | 3 | 25 | 25 | - | - | - | - | - |  |  |  |  | 2.5 TON | 111 | Base Module
0.75 | 3 | 25 | 25 | 25 | - | - | - | - |  |  |  |  | 3 TON | 141 | Base Module
1 | 3 | 39 | 39 | 39 | 39 | 39 | 39 | - |  |  |  |  | 5 TON | 198 | Base Module
1.5 | 3 | 47 | 47 | 47 | 47 | 47 | 47 | -
2 | 3 | 46 | 46 | 46 | 46 | 46 | 46 | -
3 | 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46
5 | 3 | - | 86 | 86 | 86 | 86 | 86 | 86
7.5 | 3 | - | - | 105 | 105 | 105 | 105 | 105
10 | 3 | - | - | - | 150 | 150 | 150 | 150 |  |  |  |  | PCU Blower | Weight (LBS.) | Width (IN.)
15 | 3 | - | - | - | - | 150 | 150 | 150 |  |  |  |  | KB-10 | 215.32 | 32.125
20 | 3 | - | - | - | - | 400 | 400 | 400 |  |  |  |  | KB-14 | 352.13 | 40.125
25 | 3 | - | - | - | - | - | - | 504 |  |  |  |  | KB-18 | 451.57 | 45.125
30 | 3 | - | - | - | - | - | - | 504 |  |  |  |  | KB-20 | 666.44 | 64.19
40 | 3 | - | - | - | - | - | - | 750 |  |  |  |  | KB-25 | 1069.34 | 74.19
[13 empty] | KB-25 | 1069.34 | 74.19
[13 empty] | KB-32 | 1509 | 84.19
Pre-Filter Module
[13 empty] | PF-1 | 160.73 | 26.69
[13 empty] | PF-2 | 244.12 | 26.69
[13 empty] | PF-3 | 300.87 | 31.81
[13 empty] | PF-4 | 383.2 | 28
[13 empty] | PF-5 | 427.61 | 27.56
[13 empty] | PF-6 | 585.09 | 27.56
[13 empty] | PF-7 | 811.65 | 27.56
[13 empty] | High Efficiency Module | Weight (LBS.) | Width (IN.)
[13 empty] | HE-1 | 150.23 | 26.69
[13 empty] | HE-2 | 223.12 | 26.69
[13 empty] | HE-3 | 272.87 | 31.81
[13 empty] | HE-4 | 348.2 | 28
[13 empty] | HE-5 | 385.61 | 27.56
[13 empty] | HE-6 | 522.09 | 27.56
[13 empty] | HE-7 | 706.65 | 27.56
[13 empty] | HEPA Filter Module | Weight (LBS.) | Width (IN.)
[13 empty] | HEPA-1 | 160.73 | 26.69
[13 empty] | HEPA-2 | 244.12 | 26.69
[13 empty] | HEPA-3 | 300.87 | 31.81
[13 empty] | HEPA-4 | 383.2 | 28
[13 empty] | HEPA-5 | 427.61 | 27.56
[13 empty] | HEPA-6 | 585.09 | 27.56
[13 empty] | HEAP-7 | 811.65 | 27.56
[13 empty] | Odor Control Filter LAST Module | Weight (LBS.) | Width if last module (IN.)
[13 empty] | OC-1 (Last Module) | 152.6 | 32
[13 empty] | OC-2 (Last Module) | 227.86 | 32
[13 empty] | OC-3 (Last Module) | 279.19 | 38
[13 empty] | OC-4 (Last Module) | 356.1 | 35
[13 empty] | OC-5 (Last Module) | 395.09 | 35
[13 empty] | OC-6 (Last Module) | 536.31 | 35
[13 empty] | OC-7 (Last Module) | 730.35 | 35
[13 empty] | Odor Control Filter Module | Weight (LBS.) | Width (IN.)
[13 empty] | OC-1 | 152.6 | 26.69
[13 empty] | OC-2 | 227.86 | 26.69
[13 empty] | OC-3 | 279.19 | 31.81
[13 empty] | OC-4 | 356.1 | 28
[13 empty] | OC-5 | 395.09 | 27.56
[13 empty] | OC-6 | 536.31 | 27.56
[13 empty] | OC-7 | 730.35 | 27.56
[13 empty] | Odor Control Panel Filter Module | Weight (LBS.) | Width (IN.)
[13 empty] | OCP-1 | 232.73 | 26.69
[13 empty] | OCP-2 | 388.12 | 26.69
[13 empty] | OCP-3 | 492.87 | 31.81
[13 empty] | OCP-4 | 623.2 | 28
[13 empty] | OCP-5 | 715.61 | 27.56
[13 empty] | OCP-6 | 1017.09 | 27.56
[13 empty] | OCP-7 | 1531.65 | 27.56
[13 empty] | Discharge Cover | Weight (LBS.) | Width (IN.)
[13 empty] | KB.DCS-1 | 22.11 | 22.375
[13 empty] | KB.DCS-1 | 22.11 | 22.375
[13 empty] | KB.DCS-3 | 56.15 | 34.1875
[13 empty] | KB.DCS-3 | 56.15 | 34.1875
[13 empty] | KB.DCS-3 | 56.15 | 34.1875
[13 empty] | KB.DCS-3 | 56.15 | 34.1875
[13 empty] | KB.DCS-4 | 56.15 | 34.1875
[13 empty] | Motor | Weight
[13 empty] | 0.5 HP 1 Ph | 25
[13 empty] | 0.75 HP 1 Ph | 25
[13 empty] | 1 HP 1 Ph | 33
[13 empty] | 1.5 HP 1 Ph | 32
[13 empty] | 0.5 HP 3 Ph | 25
[13 empty] | 0.75 HP 3 Ph | 25
[13 empty] | 1 HP 3 Ph | 39
[13 empty] | 1.5 HP 3 Ph | 47
[13 empty] | 2 HP 3 Ph | 46
[13 empty] | 3 HP 3 Ph | 46
[13 empty] | 5 HP 3 Ph | 86
[13 empty] | 7.5 HP 3 Ph | 105
[13 empty] | 10 HP 3 Ph | 150
[13 empty] | 15 HP 3 Ph | 150
[13 empty] | 20 HP 3 Ph | 400
[13 empty] | 25 HP 3 Ph | 504
[13 empty] | 30 HP 3 Ph | 504
[13 empty] | 40 HP 3 Ph | 750

## COM CALCULATOR EXAMPLE
MAU and PCU Center of Mass Calculator | [9 empty] | REV. #3: 03/28/2018 |  |  |  | Unit Information:
Equipment Type: | MAU | [12 empty] | MAU Module | Multiplier | Equipment Type
Position from Left: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  |  | None | 1 | MAU
Type of Module: | DX Coil Module | MAU Blower | Direct Fired Module | Intake Hood | None | None | None | None | None | None |  |  |  | MAU Blower | 0.66667 | PCU
Size: | DXM1 | 10" | D1.250 | SFIH-01M | [9 empty] | Direct Fired Module | 0.5
Motor HP (blower module only): |  | 2 HP 3 Ph | [11 empty] | Electric Heater Module | 0.5
Condenser on top of module: |  | 2.5 TON | 2.5 TON | [10 empty] | IBT Module | 0.5
Individual Weight: | 355 | 362 | 456 | 45 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summation of Loads: |  | DX Coil Module | 0.5
Individual Width: | 42.125 | 32.125 | 42.125 | 44.375 | 0 | 0 | 0 | 0 | 0 | 0 |  | 79844.2708 |  | Hot Water Coil Module | 0.5
Individual Moment | 7477.1875 | 23002.0833 | 43462.5 | 5902.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Chilled Water Coil Module | 0.5
[14 empty] | Steam Coil | 0.5
Total Weight: |  | 1218 | LBS. | [10 empty] | Standard Evaporative Intake | 0.5
Center Of Mass: |  | 65.5536 | INCHES (Distance from left side of Unit) | [10 empty] | Celdek Evaporative Intake | 0.5
Intake End Corner Weights |  | 343.0474 | LBS. (Standard Right > Left Config Assumed) | [10 empty] | V-Bank Filter Intake | 0.5
Discharge End Corner Weights |  | 265.9526 | LBS. (Standard Right > Left Config Assumed) | [10 empty] | Screened Intake | 0.33333
[14 empty] | Intake Hood | 0.33333
[14 empty] | Downturn Plenum | 0.5
|  |  | Calculation Steps: | [10 empty] | Trunkline | 0.5
|  |  | Step #1: Select if the unit is a MAU or PCU in cell B3. | [10 empty] | Mixing box/Condenser support | 0.5
|  |  | Step #2: Generate a drawing of the unit in Nola and enter the modules in rows 5 and 6 in order from left to right. This calculator assumes the unit is standard airflow from right to left. Note that some modules may have to be searched in the BOM of the fan such as the intake module and coil modules. |  |  | BOM Search Example for Step #2: | [7 empty] | PCU Module | Multiplier
[14 empty] | None | 1
[14 empty] | PCU Blower | 0.66667
[14 empty] | Pre-Filter Module | 0.5
|  |  | Step #3: For the blower module, select the Motor HP from row 7. If a module has a condenser ontop of it, select the condenser's tonnage in row 8. | [10 empty] | High Efficiency Module | 0.5
[14 empty] | HEPA Filter Module | 0.5
[14 empty] | Odor Control Filter Module | 0.5
|  |  | Step #4: Reference the Individual modules' weight and width in rows 9 and 10. Total Weight, Center Of Mass, and Corner Weights for the entire unit will be displayed in the light blue output cells (C13:C16). | [10 empty] | Odor Control Filter LAST Module | 0.5
[14 empty] | Odor Control Panel Filter Module | 0.5
[14 empty] | Discharge Cover | 0.33333
Makeup Air Individual Module Reference Information:
BLOWER MODULES:
Unit Spec | Blower Size
| 10" | 12" | 15" | 15"D | 18" | 20" | 20"D | 24"D | 25" | 30"D | 36"D |  | MAU Blower | Weight (LBS.) | Width (IN.)
Weight (LBS.) | 205 | 350 | 360 | 260 | 435 | 735 | 428 | 531 | 1105 | 1067 | 1271 |  | 10" | 205 | 32.125
Width (IN.) | 32.125 | 40.125 | 40.125 | 32.125 | 45.125 | 64.1875 | 40.125 | 45.125 | 74.1875 | 64.1875 | 74.1875 |  | 12" | 350 | 40.125
[13 empty] | 15" | 360 | 40.125
DIRECT FIRED HEATING MODULES: | [12 empty] | 15"D | 260 | 32.125
Unit Spec | Model | [11 empty] | 18" | 435 | 45.125
| D1.250 | D1.500 | D2.500 | D2.750 | D3.750 | D3.1000 | D4.1000 | D4.1500 | D5.2000 | D5.2500 |  |  | 20" | 735 | 64.1875
Weight (LBS.) | 345 | 350 | 420 | 425 | 450 | 455 | 690 | 705 | 830 | 845 |  |  | 20"D | 428 | 40.125
Width (IN.) | 42.125 | 42.125 | 42.125 | 42.125 | 42.125 | 42.125 | 54.1875 | 54.1875 | 54.1875 | 54.1875 |  |  | 24"D | 531 | 45.125
[13 empty] | 25" | 1105 | 74.1875
[13 empty] | 30"D | 1067 | 64.1875
ELECTRIC HEATER MODULES: | [12 empty] | 36"D | 1271 | 74.1875
Unit Spec | Model
| E1.10 | E1.20 | E1.204 | E1.36 | E2.36 | E2.69 | E3.83 | E4.155 | E5.235
Weight (LBS.) | 300 | 300 | 300 | 300 | 380 | 380 | 450 | 710 | 840 |  |  |  | Direct Fired Module
Width (IN.) | 42.125 | 42.125 | 42.125 | 42.125 | 42.125 | 42.125 | 42.125 | 54.1875 | 54.1875 |  |  |  | D1.250 | 345 | 42.125
[13 empty] | D1.500 | 350 | 42.125
[13 empty] | D2.500 | 420 | 42.125
INDIRECT FIRED HEATING MODULES: | [12 empty] | D2.750 | 425 | 42.125
Unit Spec | Model IBT | [11 empty] | D3.750 | 450 | 42.125
| 1-.150 | 1-.200 | 1-.300-150-150 | 1-.400-200-200 | 2-.200 | 2-.300 | 2-.400 | 2-.400-200-200 | 2-.600-300-300 |  |  |  | D3.1000 | 455 | 42.125
Weight (LBS.) | 567 | 597 | 652 | 726 | 595 | 687 | 766 | 654 | 808 |  |  |  | D4.1000 | 690 | 54.1875
Width (IN.) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  |  |  | D4.1500 | 705 | 54.1875
[13 empty] | D5.2000 | 830 | 54.1875
| 2-.800-400-400 | 3-.400 | 3.-600-300-300 | 3.-800-400-400 | 3.-1000-300-300-400 | 3.-1200-400-400-400 | 4.-800-400-400 | 4.1000-300-300-400 | 4.-1200-400-400-400 |  |  |  | D5.2500 | 845 | 54.1875
Weight (LBS.) | 921 | 947 | 1065 | 1203 | 1942 | 2054 | 1154 | 2037 | 2149
Width (IN.) | 60 | 60 | 60 | 60 | 120 | 120 | 120 | 120 | 120
| 4.-1400-300-300-400-400 | 4.-1600-400-400-400-400 | 5-.800-400-400 | 5.-1000-300-300-400 | 5.-1200-400-400-400 | 5.-1400-300-300-400-400 | 5.-1600-400-400-400-400 | [5 empty] | Electric Heater Module
Weight (LBS.) | 2261 | 2373 | 1257 | 2029 | 2141 | 2253 | 2365 | [5 empty] | E1.10 | 300 | 42.125
Width (IN.) | 120 | 120 | 60 | 120 | 120 | 120 | 120 | [5 empty] | E1.20 | 300 | 42.125
[13 empty] | E1.204 | 300 | 42.125
[13 empty] | E1.36 | 300 | 42.125
DX COIL MODULES: | [12 empty] | E2.36 | 380 | 42.125
Unit Spec | Model | [11 empty] | E2.69 | 380 | 42.125
| DXM1 | DXM2 | DXM3 | DXM4 | DXM5 | [7 empty] | E3.83 | 450 | 42.125
Weight (LBS.) | 355 | 430 | 505 | 780 | 905 | [7 empty] | E4.155 | 710 | 54.1875
Width (IN.) | 42.125 | 42.125 | 42.125 | 54.1875 | 54.1875 | [7 empty] | E5.235 | 840 | 54.1875
HOT WATER COIL MODULES: | [12 empty] | IBT Module
Unit Spec | Model | [11 empty] | 1-.150 | 567 | 52
| HWCM1 | HWCM2 | HWCM3 | HWCM4 | HWCM5 | [7 empty] | 1-.200 | 597 | 52
Weight (LBS.) | 160 | 220 | 260 | 435 | 525 | [7 empty] | 1-.300-150-150 | 652 | 52
Width (IN.) | 42.125 | 42.125 | 42.125 | 54.1875 | 54.1875 | [7 empty] | 1-.400-200-200 | 726 | 52
[13 empty] | 2-.200 | 595 | 52
[13 empty] | 2-.300 | 687 | 52
CHILLED WATER COIL MODULES: | [12 empty] | 2-.400 | 766 | 52
Unit Spec | Model | [11 empty] | 2-.400-200-200 | 654 | 52
| CWCM1 | CWCM2 | CWCM3 | CWCM4 | CWCM5 | [7 empty] | 2-.600-300-300 | 808 | 52
Weight (LBS.) | 355 | 435 | 575 | 790 | 905 | [7 empty] | 2-.800-400-400 | 921 | 52
Width (IN.) | 42.125 | 42.125 | 42.125 | 54.1875 | 54.1875 | [7 empty] | 3-.400 | 947 | 52
[13 empty] | 3.-600-300-300 | 1065 | 52
[13 empty] | 3.-800-400-400 | 1203 | 52
STEAM COIL MODULES: | [12 empty] | 3.-1000-300-300-400 | 1942 | 112.125
Unit Spec | Model | [11 empty] | 3.-1200-400-400-400 | 2054 | 112.125
| SCM1 | SCM2 | SCM3 | SCM4 | SCM5 | [7 empty] | 4.-800-400-400 | 1154 | 52
Weight (LBS.) | 160 | 220 | 255 | 410 | 520 | [7 empty] | 4.1000-300-300-400 | 2037 | 112.125
Width (IN.) | 42.125 | 42.125 | 42.125 | 54.1875 | 54.1875 | [7 empty] | 4.-1200-400-400-400 | 2149 | 112.125
[13 empty] | 4.-1400-300-300-400-400 | 2261 | 112.125
[13 empty] | 4.-1600-400-400-400-400 | 2373 | 112.125
STANDARD EVAPORATIVE COOLER INTAKE: | [12 empty] | 5-.800-400-400 | 1257 | 52
Unit Spec | Model | [11 empty] | 5.-1000-300-300-400 | 2029 | 112.125
| ECI-01 | ECI-02 | ECI-03 | ECI-04 | ECI-05 | [7 empty] | 5.-1200-400-400-400 | 2141 | 112.125
Weight (LBS.) | 130 | 180 | 240 | 330 | 405 | [7 empty] | 5.-1400-300-300-400-400 | 2253 | 112.125
Width (IN.) | 32.125 | 32.125 | 38.125 | 35.25 | 35.25 | [7 empty] | 5.-1600-400-400-400-400 | 2365 | 112.125
CELDEK EVAPORATIVE COOLER INTAKE: | [12 empty] | DX Coil Module
Unit Spec | Model | [11 empty] | DXM1 | 355 | 42.125
| CDI-01 | CDI-02 | CDI-03 | CDI-04 | CDI-05 | [7 empty] | DXM2 | 430 | 42.125
Weight (LBS.) | 135 | 175 | 230 | 300 | 365 | [7 empty] | DXM3 | 505 | 42.125
Width (IN.) | 32.125 | 32.125 | 38.125 | 35.25 | 35.25 | [7 empty] | DXM4 | 780 | 54.1875
[13 empty] | DXM5 | 905 | 54.1875
V-BANK FILTER INTAKE:
Unit Spec | Model | [11 empty] | Hot Water Coil Module
| VBI-01 | VBI-02 | VBI-03 | VBI-04 | VBI-05 | [7 empty] | HWCM1 | 160 | 42.125
Weight (LBS.) | 95 | 135 | 165 | 235 | 295 | [7 empty] | HWCM2 | 220 | 42.125
Width (IN.) | 32.125 | 32.125 | 38.125 | 35.25 | 35.25 | [7 empty] | HWCM3 | 260 | 42.125
[13 empty] | HWCM4 | 435 | 54.1875
[13 empty] | HWCM5 | 525 | 54.1875
SCREENED INTAKE:
Unit Spec | Model
| SI-1 | SI-2 | SI-3 | SI-4 | SI-5 | [7 empty] | Chilled Water Coil Module
Weight (LBS.) | 25 | 35 | 50 | 100 | 135 | [7 empty] | CWCM1 | 355 | 42.125
Width (IN.) | 22.375 | 30.3125 | 34.1875 | 47.25 | 49.625 | [7 empty] | CWCM2 | 435 | 42.125
[13 empty] | CWCM3 | 575 | 42.125
[13 empty] | CWCM4 | 790 | 54.1875
INTAKE HOOD: | [12 empty] | CWCM5 | 905 | 54.1875
Unit Spec | Model
| SFIH-01M | SFIH-02M | SFIH-03M | SFIH-04M | SFIH-05M | SFIH-01S | SFIH-02S
Weight (LBS.) | 45 | 65 | 90 | 210 | 225 | 30 | 40 | [5 empty] | Steam Coil
Width (IN.) | 44.375 | 53.625 | 51.625 | 76.375 | 71.375 | 25.875 | 29.25 | [5 empty] | SCM1 | 160 | 42.125
[13 empty] | SCM2 | 220 | 42.125
[13 empty] | SCM3 | 255 | 42.125
DOWNTURN PLENUM: | [12 empty] | SCM4 | 410 | 54.1875
Unit Spec | Model | [11 empty] | SCM5 | 520 | 54.1875
| DP-01 | DP-02 | DP-03 | DP-04 | DP-05
Weight (LBS.) | 80 | 115 | 140 | 190 | 230
Width (IN.) | 18.25 | 24.25 | 24.25 | 30.25 | 30.25 | [7 empty] | Standard Evaporative Intake
[13 empty] | ECI-01 | 130 | 32.125
[13 empty] | ECI-02 | 180 | 32.125
TRUNKLINE: | [12 empty] | ECI-03 | 240 | 38.125
Unit Spec | Model | [11 empty] | ECI-04 | 330 | 35.25
| TL-01M | TL-02M | TL-03M | TL-04M | TL-01S | TL-02S | TL-01DF | TL-02DF | TL-03DF |  |  |  | ECI-05 | 405 | 35.25
Weight (LBS.) | 135 | 175 | 215 | 310 | 120 | 175 | 95 | 120 | 150
Width (IN.) | 88 | 80 | 75 | 50 | 88 | 80 | 46 | 38 | 33
Celdek Evaporative Intake
[13 empty] | CDI-01 | 135 | 32.125
MIXING BOX/CONDENSER SUPPORT: | [12 empty] | CDI-02 | 175 | 32.125
Unit Spec | Model TL-01M: Model |  |  |  | CDI-03 | 230 | 38.125
| Model TL-01M: MB-1; Model TL-02M: MB-2; Model TL-03M: MB-3; Model TL-04M: MB-4; Model TL-01S: MB-5 |  |  |  | CDI-04 | 300 | 35.25
Weight (LBS.) | Model TL-01M: 155; Model TL-02M: 215; Model TL-03M: 280; Model TL-04M: 475; Model TL-01S: 575 |  |  |  | CDI-05 | 365 | 35.25
Width (IN.) | Model TL-01M: 42.125; Model TL-02M: 42.125; Model TL-03M: 42.125; Model TL-04M: 54.1875; Model TL-01S: 54.1875
V-Bank Filter Intake
CONDENSERS: | [12 empty] | VBI-01 | 95 | 32.125
Unit Spec | Model TL-01M: Model |  |  |  | VBI-02 | 135 | 32.125
| Model TL-01M: 2 TON; Model TL-02M: 2.5 TON; Model TL-03M: 3 TON; Model TL-04M: 5 TON |  |  |  | VBI-03 | 165 | 38.125
Weight (LBS.) | Model TL-01M: 110; Model TL-02M: 111; Model TL-03M: 141; Model TL-04M: 198; Model TL-01S: Add the condenser weight to the module that it is supported by. Use the support module |  |  |  | VBI-04 | 235 | 35.25
Width (IN.) | Model TL-01M: Base Module; Model TL-02M: Base Module; Model TL-03M: Base Module; Model TL-04M: Base Module; Model TL-01S: width for dimensional data. |  |  |  | VBI-05 | 295 | 35.25
Pollution Control Unit Individual Module Reference Information: | [12 empty] | Screened Intake
[13 empty] | SI-1 | 25 | 22.375
POLLUTION CONTROL UNIT - BLOWER | [12 empty] | SI-2 | 35 | 30.3125
Unit Spec | Model TL-01M: Blower Size |  |  |  | SI-3 | 50 | 34.1875
| KB-10 | KB-14 | KB-18 | KB-20 | KB-25 | KB-25 | KB-32 | [5 empty] | SI-4 | 100 | 47.25
Weight (LBS.) | 215.32 | 352.13 | 451.57 | 666.44 | 1069.34 | 1069.34 | 1509 | [5 empty] | SI-5 | 135 | 49.625
Width (IN.) | 32.125 | 40.125 | 45.125 | 64.19 | 74.19 | 74.19 | 84.19
POLLUTION CONTROL UNIT - PREFILTER
Unit Spec | Model TL-01M: Model |  |  |  | Intake Hood
| PF-1 | PF-2 | PF-3 | PF-4 | PF-5 | PF-6 | PF-7 | [5 empty] | SFIH-01M | 45 | 44.375
Weight (LBS.) | 160.73 | 244.12 | 300.87 | 383.2 | 427.61 | 585.09 | 811.65 | [5 empty] | SFIH-02M | 65 | 53.625
Width (IN.) | 26.69 | 26.69 | 31.81 | 28 | 27.56 | 27.56 | 27.56 | [5 empty] | SFIH-03M | 90 | 51.625
[13 empty] | SFIH-04M | 210 | 76.375
POLLUTION CONTROL UNIT - HIGH EFFICIENCY FILTER | [12 empty] | SFIH-05M | 225 | 71.375
Unit Spec | Model TL-01M: Model |  |  |  | SFIH-01S | 30 | 25.875
| HE-1 | HE-2 | HE-3 | HE-4 | HE-5 | HE-6 | HE-7 | [5 empty] | SFIH-02S | 40 | 29.25
Weight (LBS.) | 150.23 | 223.12 | 272.87 | 348.2 | 385.61 | 522.09 | 706.65
Width (IN.) | 26.69 | 26.69 | 31.81 | 28 | 27.56 | 27.56 | 27.56
Downturn Plenum
POLLUTION CONTROL UNIT - HEPA FILTER | [12 empty] | DP-01 | 80 | 18.25
Unit Spec | Model TL-01M: Model |  |  |  | DP-02 | 115 | 24.25
| HEPA-1 | HEPA-2 | HEPA-3 | HEPA-4 | HEPA-5 | HEPA-6 | HEAP-7 | [5 empty] | DP-03 | 140 | 24.25
Weight (LBS.) | 160.73 | 244.12 | 300.87 | 383.2 | 427.61 | 585.09 | 811.65 | [5 empty] | DP-04 | 190 | 30.25
Width (IN.) | 26.69 | 26.69 | 31.81 | 28 | 27.56 | 27.56 | 27.56 | [5 empty] | DP-05 | 230 | 30.25
POLLUTION CONTROL UNIT - ODOR CONTROL FILTER
Unit Spec | Model TL-01M: Model |  |  |  | Trunkline
| OC-1 | OC-2 | OC-3 | OC-4 | OC-5 | OC-6 | OC-7 | [5 empty] | TL-01M | 135 | 88
Weight (LBS.) | 152.6 | 227.86 | 279.19 | 356.1 | 395.09 | 536.31 | 730.35 | [5 empty] | TL-02M | 175 | 80
Width (IN.) | 26.69 | 26.69 | 31.81 | 28 | 27.56 | 27.56 | 27.56 | [5 empty] | TL-03M | 215 | 75
Width if last module (IN.) | 32 | 32 | 38 | 35 | 35 | 35 | 35 | [5 empty] | TL-04M | 310 | 50
[13 empty] | TL-01S | 120 | 88
POLLUTION CONTROL UNIT - ODOR CONTROL PANEL FILTER | [12 empty] | TL-02S | 175 | 80
Unit Spec | Model TL-01M: Model |  |  |  | TL-01DF | 95 | 46
| OCP-1 | OCP-2 | OCP-3 | OCP-4 | OCP-5 | OCP-6 | OCP-7 | [5 empty] | TL-02DF | 120 | 38
Weight (LBS.) | 232.73 | 388.12 | 492.87 | 623.2 | 715.61 | 1017.09 | 1531.65 | [5 empty] | TL-03DF | 150 | 33
Width (IN.) | 26.69 | 26.69 | 31.81 | 28 | 27.56 | 27.56 | 27.56
DISCHARGE COVER - Use Triangular Intake setting | [12 empty] | Mixing box/Condenser support
Unit Spec | Model TL-01M: Model |  |  |  | MB-1 | 155 | 42.125
| KB.DCS-1 | KB.DCS-1 | KB.DCS-3 | KB.DCS-3 | KB.DCS-3 | KB.DCS-3 | KB.DCS-4 | [5 empty] | MB-2 | 215 | 42.125
Weight (LBS.) | 22.11 | 22.11 | 56.15 | 56.15 | 56.15 | 56.15 | 56.15 | [5 empty] | MB-3 | 280 | 42.125
Width (IN.) | 22.375 | 22.375 | 34.1875 | 34.1875 | 34.1875 | 34.1875 | 34.1875 | [5 empty] | MB-4 | 475 | 54.1875
[13 empty] | MB-5 | 575 | 54.1875
POLLUTION CONTROL UNIT - MOTOR WEIGHT - add to the blower weight
HP | Model TL-01M: Phase; Model TL-02M: Model |  |  |  | Condensers
|  | KB-10 | KB-14 | KB-18 | KB-20 | KB-25 | KB-25 | KB-32
0.5 | 1 | 25 | 25 | - | - | - | - | - |  |  |  |  | 2 TON | 110 | Base Module
0.75 | 1 | 25 | 25 | 25 | - | - | - | - |  |  |  |  | 2.5 TON | 111 | Base Module
1 | 1 | 33 | 33 | 33 | 33 | 33 | 33 | - |  |  |  |  | 3 TON | 141 | Base Module
1.5 | 1 | 32 | 32 | 32 | 32 | 32 | 32 | - |  |  |  |  | 5 TON | 198 | Base Module
0.5 | 3 | 25 | 25 | - | - | - | - | -
0.75 | 3 | 25 | 25 | 25 | - | - | - | -
1 | 3 | 39 | 39 | 39 | 39 | 39 | 39 | -
1.5 | 3 | 47 | 47 | 47 | 47 | 47 | 47 | -
2 | 3 | 46 | 46 | 46 | 46 | 46 | 46 | -
3 | 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  |  |  |  | PCU Blower | Weight (LBS.) | Width (IN.)
5 | 3 | - | 86 | 86 | 86 | 86 | 86 | 86 |  |  |  |  | KB-10 | 215.32 | 32.125
7.5 | 3 | - | - | 105 | 105 | 105 | 105 | 105 |  |  |  |  | KB-14 | 352.13 | 40.125
10 | 3 | - | - | - | 150 | 150 | 150 | 150 |  |  |  |  | KB-18 | 451.57 | 45.125
15 | 3 | - | - | - | - | 150 | 150 | 150 |  |  |  |  | KB-20 | 666.44 | 64.19
20 | 3 | - | - | - | - | 400 | 400 | 400 |  |  |  |  | KB-25 | 1069.34 | 74.19
25 | 3 | - | - | - | - | - | - | 504 |  |  |  |  | KB-25 | 1069.34 | 74.19
30 | 3 | - | - | - | - | - | - | 504 |  |  |  |  | KB-32 | 1509 | 84.19
40 | 3 | - | - | - | - | - | - | 750
Pre-Filter Module
[13 empty] | PF-1 | 160.73 | 26.69
[13 empty] | PF-2 | 244.12 | 26.69
[13 empty] | PF-3 | 300.87 | 31.81
[13 empty] | PF-4 | 383.2 | 28
[13 empty] | PF-5 | 427.61 | 27.56
[13 empty] | PF-6 | 585.09 | 27.56
[13 empty] | PF-7 | 811.65 | 27.56
[13 empty] | High Efficiency Module | Weight (LBS.) | Width (IN.)
[13 empty] | HE-1 | 150.23 | 26.69
[13 empty] | HE-2 | 223.12 | 26.69
[13 empty] | HE-3 | 272.87 | 31.81
[13 empty] | HE-4 | 348.2 | 28
[13 empty] | HE-5 | 385.61 | 27.56
[13 empty] | HE-6 | 522.09 | 27.56
[13 empty] | HE-7 | 706.65 | 27.56
[13 empty] | HEPA Filter Module | Weight (LBS.) | Width (IN.)
[13 empty] | HEPA-1 | 160.73 | 26.69
[13 empty] | HEPA-2 | 244.12 | 26.69
[13 empty] | HEPA-3 | 300.87 | 31.81
[13 empty] | HEPA-4 | 383.2 | 28
[13 empty] | HEPA-5 | 427.61 | 27.56
[13 empty] | HEPA-6 | 585.09 | 27.56
[13 empty] | HEAP-7 | 811.65 | 27.56
[13 empty] | Odor Control Filter LAST Module | Weight (LBS.) | Width if last module (IN.)
[13 empty] | OC-1 (Last Module) | 152.6 | 32
[13 empty] | OC-2 (Last Module) | 227.86 | 32
[13 empty] | OC-3 (Last Module) | 279.19 | 38
[13 empty] | OC-4 (Last Module) | 356.1 | 35
[13 empty] | OC-5 (Last Module) | 395.09 | 35
[13 empty] | OC-6 (Last Module) | 536.31 | 35
[13 empty] | OC-7 (Last Module) | 730.35 | 35
[13 empty] | Odor Control Filter Module | Weight (LBS.) | Width (IN.)
[13 empty] | OC-1 | 152.6 | 26.69
[13 empty] | OC-2 | 227.86 | 26.69
[13 empty] | OC-3 | 279.19 | 31.81
[13 empty] | OC-4 | 356.1 | 28
[13 empty] | OC-5 | 395.09 | 27.56
[13 empty] | OC-6 | 536.31 | 27.56
[13 empty] | OC-7 | 730.35 | 27.56
[13 empty] | Odor Control Panel Filter Module | Weight (LBS.) | Width (IN.)
[13 empty] | OCP-1 | 232.73 | 26.69
[13 empty] | OCP-2 | 388.12 | 26.69
[13 empty] | OCP-3 | 492.87 | 31.81
[13 empty] | OCP-4 | 623.2 | 28
[13 empty] | OCP-5 | 715.61 | 27.56
[13 empty] | OCP-6 | 1017.09 | 27.56
[13 empty] | OCP-7 | 1531.65 | 27.56
[13 empty] | Discharge Cover | Weight (LBS.) | Width (IN.)
[13 empty] | KB.DCS-1 | 22.11 | 22.375
[13 empty] | KB.DCS-1 | 22.11 | 22.375
[13 empty] | KB.DCS-3 | 56.15 | 34.1875
[13 empty] | KB.DCS-3 | 56.15 | 34.1875
[13 empty] | KB.DCS-3 | 56.15 | 34.1875
[13 empty] | KB.DCS-3 | 56.15 | 34.1875
[13 empty] | KB.DCS-4 | 56.15 | 34.1875
[13 empty] | Motor | Weight
[13 empty] | 0.5 HP 1 Ph | 25
[13 empty] | 0.75 HP 1 Ph | 25
[13 empty] | 1 HP 1 Ph | 33
[13 empty] | 1.5 HP 1 Ph | 32
[13 empty] | 0.5 HP 3 Ph | 25
[13 empty] | 0.75 HP 3 Ph | 25
[13 empty] | 1 HP 3 Ph | 39
[13 empty] | 1.5 HP 3 Ph | 47
[13 empty] | 2 HP 3 Ph | 46
[13 empty] | 3 HP 3 Ph | 46
[13 empty] | 5 HP 3 Ph | 86
[13 empty] | 7.5 HP 3 Ph | 105
[13 empty] | 10 HP 3 Ph | 150
[13 empty] | 15 HP 3 Ph | 150
[13 empty] | 20 HP 3 Ph | 400
[13 empty] | 25 HP 3 Ph | 504
[13 empty] | 30 HP 3 Ph | 504
[13 empty] | 40 HP 3 Ph | 750